## Protocol 5016
Modbus-Address | Size | Index | Description | Unit | Scale
Topic Alarm Management
Subtopic General
50114 | uint16 | 10131 | BITLIST Alarm General
|  |  | 01.11 New Alarm triggered |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Internal |  | Mask: 0100h
|  |  | Internal |  | Mask: 0080h
|  |  | Internal |  | Mask: 0040h
|  |  | 01.06 Alarm class F latched |  | Mask: 0020h
|  |  | 01.05 Alarm class E latched |  | Mask: 0010h
|  |  | 01.04 Alarm class D latched |  | Mask: 0008h
|  |  | 01.03 Alarm class C latched |  | Mask: 0004h
|  |  | 01.02 Alarm class B latched |  | Mask: 0002h
|  |  | 01.01 Alarm class A latched |  | Mask: 0001h
50115 | uint16 | 10149 | BITLIST Alarms 2 latched (unacknowledged)
|  |  | 08.30 Timeout Synchronisation GCB latched |  | Mask: 8000h
|  |  | 08.31 Timeout Synchronisation MCB latched |  | Mask: 4000h
|  |  | 08.32 Timeout Synchronisation GGB latched |  | Mask: 2000h
|  |  | 05.11 Charge fail (D+ functionality) latched |  | Mask: 1000h
|  |  | Operating range failure 12 latched |  | Mask: 0800h
|  |  | 08.45 CPU overload R1 trip latched |  | Mask: 0400h
|  |  | 08.47 MCB failure 50BF |  | Mask: 0200h
|  |  | 08.46 GCB failure 50BF |  | Mask: 0100h
|  |  | 05.22 ECU Protect alarm |  | Mask: 0080h
|  |  | 05.23 ECU Emission alarm |  | Mask: 0040h
|  |  | 08.19 CANopen error at CAN Interface 2 |  | Mask: 0020h
|  |  | 08.16 Parameter Alignment LDSS |  | Mask: 0010h
|  |  | 08.17 Missing members |  | Mask: 0008h
|  |  | 08.48 MCB plausibility |  | Mask: 0004h
|  |  | 05.13 ECU red lamp alarm latched |  | Mask: 0002h
|  |  | 05.14 ECU yellow (amber) lamp alarm latched |  | Mask: 0001h
50116 | uint16 | 4169 | BITLIST Alarms 2 active
|  |  | Timeout Synchronisation GCB |  | Mask: 8000h
|  |  | Timeout Synchronisation MCB |  | Mask: 4000h
|  |  | Timeout Synchronisation GGB |  | Mask: 2000h
|  |  | Charge fail (D+ functionality) |  | Mask: 1000h
|  |  | Gen/Busbar/Mains phase rotat. |  | Mask: 0800h
|  |  | CPU overload R1 trip |  | Mask: 0400h
|  |  | MCB failure 50BF |  | Mask: 0200h
|  |  | GCB failure 50BF |  | Mask: 0100h
|  |  | ECU Protect alarm |  | Mask: 0080h
|  |  | ECU Emission alarm |  | Mask: 0040h
|  |  | CANopen error at CAN Interface 2 |  | Mask: 0020h
|  |  | Parameter Alignment LDSS |  | Mask: 0010h
|  |  | Missing members |  | Mask: 0008h
|  |  | MCB plausibility |  | Mask: 0004h
|  |  | ECU red lamp alarm |  | Mask: 0002h
|  |  | ECU yellow (amber) lamp alarm |  | Mask: 0001h
50117 | uint16 | 10190 | BITLIST Alarms 3 latched (unacknowledged)
|  |  | 08.34 GGB fail to close latched |  | Mask: 8000h
|  |  | 08.35 GGB fail to open latched |  | Mask: 4000h
|  |  | 08.27 Missing easYgen |  | Mask: 2000h
|  |  | 08.28 Missing LS5 |  | Mask: 1000h
|  |  | 05.18 Cylinder temperature level 1 |  | Mask: 0800h
|  |  | 05.19 Cylinder temperature level 2 |  | Mask: 0400h
|  |  | 05.20 Cylinder temperature wire break |  | Mask: 0200h
|  |  | 6.35 Pole slip |  | Mask: 0100h
|  |  | 08.44 Syst.update LS5 |  | Mask: 0080h
|  |  | 08.43 Syst.update easYgen |  | Mask: 0040h
|  |  | 06.32 Gen.AC Wiring |  | Mask: 0020h
|  |  | 06.33 Busbar1 AC Wiring |  | Mask: 0010h
|  |  | 08.29 CANopen error interface 3 |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50118 | uint16 | 4193 | BITLIST Alarms 3 active
|  |  | GGB fail to close |  | Mask: 8000h
|  |  | GGB fail to open |  | Mask: 4000h
|  |  | Missing easYgen |  | Mask: 2000h
|  |  | Missing LS5 |  | Mask: 1000h
|  |  | Temperature deviation level 1 |  | Mask: 0800h
|  |  | Temperature deviation level 2 |  | Mask: 0400h
|  |  | Temperature deviation wire break |  | Mask: 0200h
|  |  | Pole slip |  | Mask: 0100h
|  |  | Syst.update LS5 |  | Mask: 0080h
|  |  | Syst.update easYgen |  | Mask: 0040h
|  |  | Gen.AC Wiring |  | Mask: 0020h
|  |  | Busbar1 AC Wiring |  | Mask: 0010h
|  |  | CANopen error interface 3 |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50119 | uint16 | 4086 | BITLIST ControlBits8
|  |  | Operating Range Monitoring Code Number |  | Mask: FF00h
|  |  | The current segment number |  | Mask: 00FFh
Subtopic Engine
50120 | uint16 | 10133 | BITLIST Alarms 1 latched (unacknowledged)
|  |  | 05.01 Engine Over speed 1 latched |  | Mask: 8000h
|  |  | 05.02 Engine Over speed 2 latched |  | Mask: 4000h
|  |  | 05.03 Engine under speed 1 latched |  | Mask: 2000h
|  |  | 05.04 Engine under speed 2 latched |  | Mask: 1000h
|  |  | 05.05 Unintended stop detected latched |  | Mask: 0800h
|  |  | 05.07 Speed detection alarm latched |  | Mask: 0400h
|  |  | 05.06 Shutdown malfunction detected latched |  | Mask: 0200h
|  |  | 08.05 GCB fail to close latched |  | Mask: 0100h
|  |  | 08.06 GCB fail to open latched |  | Mask: 0080h
|  |  | 08.07 MCB fail to close latched |  | Mask: 0040h
|  |  | 08.08 MCB fail to open latched |  | Mask: 0020h
|  |  | 08.10 General CAN-J1939 fault latched |  | Mask: 0010h
|  |  | 05.08 Start fail detected latched |  | Mask: 0008h
|  |  | 05.09 Maintenance days exceeded latched |  | Mask: 0004h
|  |  | 05.10 Maintenance hours exceeded latched |  | Mask: 0002h
|  |  | 08.18 CANopen error at CAN Interface 1 |  | Mask: 0001h
50121 | uint16 | 4167 | BITLIST Alarms 1 active
|  |  | Engine Over speed 1 |  | Mask: 8000h
|  |  | Engine Over speed 2 |  | Mask: 4000h
|  |  | Engine under speed 1 |  | Mask: 2000h
|  |  | Engine under speed 2 |  | Mask: 1000h
|  |  | Unintended stop detected |  | Mask: 0800h
|  |  | Speed detection alarm |  | Mask: 0400h
|  |  | Shutdown malfunction detected |  | Mask: 0200h
|  |  | GCB fail to close |  | Mask: 0100h
|  |  | GCB fail to open |  | Mask: 0080h
|  |  | MCB fail to close |  | Mask: 0040h
|  |  | MCB fail to open |  | Mask: 0020h
|  |  | General CAN-J1939 fault |  | Mask: 0010h
|  |  | Start fail detected |  | Mask: 0008h
|  |  | Maintenance days exceeded |  | Mask: 0004h
|  |  | Maintenance hours exceeded |  | Mask: 0002h
|  |  | CANopen error at CAN Interface 1 |  | Mask: 0001h
50122 | uint16 | 10136 | BITLIST Alarms AI 1 latched (unacknowledged)
|  |  | Internal |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Internal |  | Mask: 0100h
|  |  | Internal |  | Mask: 0080h
|  |  | Internal |  | Mask: 0040h
|  |  | Internal |  | Mask: 0020h
|  |  | 05.11 Failure Charging Alternator (D+) |  | Mask: 0010h
|  |  | 08.02 Battery over voltage 2 latched |  | Mask: 0008h
|  |  | 08.04 Battery under voltage 2 latched |  | Mask: 0004h
|  |  | 08.01 Battery over voltage 1 latched |  | Mask: 0002h
|  |  | 08.03 Battery under voltage 1 latched |  | Mask: 0001h
50123 | uint16 | 4171 | BITLIST Alarms Analog Inputs 1 active
|  |  | Internal |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Internal |  | Mask: 0100h
|  |  | Internal |  | Mask: 0080h
|  |  | Internal |  | Mask: 0040h
|  |  | Internal |  | Mask: 0020h
|  |  | Failure Charging Alternator (D+) |  | Mask: 0010h
|  |  | Battery over voltage 2 |  | Mask: 0008h
|  |  | Battery under voltage 2 |  | Mask: 0004h
|  |  | Battery over voltage 1 |  | Mask: 0002h
|  |  | Battery under voltage 1 |  | Mask: 0001h
50124 | int16 |  | Internal
50125 | int16 |  | Internal
Subtopic Generator
50126 | uint16 | 10134 | BITLIST Alarms Gen latched (unacknowledged)
|  |  | 06.01 Generator over frequency 1 latched |  | Mask: 8000h
|  |  | 06.02 Generator over frequency 2 latched |  | Mask: 4000h
|  |  | 06.03 Generator under frequency 1 latched |  | Mask: 2000h
|  |  | 06.04 Generator under frequency 2 latched |  | Mask: 1000h
|  |  | 06.05 Generator over voltage 1 latched |  | Mask: 0800h
|  |  | 06.06 Generator over voltage 2 latched |  | Mask: 0400h
|  |  | 06.07 Generator under voltage 1 latched |  | Mask: 0200h
|  |  | 06.08 Generator under voltage 2 latched |  | Mask: 0100h
|  |  | 06.09 Generator over current 1 latched |  | Mask: 0080h
|  |  | 06.10 Generator over current 2 latched |  | Mask: 0040h
|  |  | 06.11 Generator over current 3 latched |  | Mask: 0020h
|  |  | 06.12 Reverse / reduced power 1 latched |  | Mask: 0010h
|  |  | 06.13 Reverse / reduced power 2 latched |  | Mask: 0008h
|  |  | 06.14 Generator overload IOP 1 latched |  | Mask: 0004h
|  |  | 06.15 Generator overload IOP 2 latched |  | Mask: 0002h
|  |  | 06.34 Busbar phase rotation mismatch latched |  | Mask: 0001h
50127 | uint16 | 4161 | BITLIST Alarms Generator active
|  |  | Generator over frequency 1 |  | Mask: 8000h
|  |  | Generator over frequency 2 |  | Mask: 4000h
|  |  | Generator under frequency 1 |  | Mask: 2000h
|  |  | Generator under frequency 2 |  | Mask: 1000h
|  |  | Generator over voltage 1 |  | Mask: 0800h
|  |  | Generator over voltage 2 |  | Mask: 0400h
|  |  | Generator under voltage 1 |  | Mask: 0200h
|  |  | Generator under voltage 2 |  | Mask: 0100h
|  |  | Generator over current 1 |  | Mask: 0080h
|  |  | Generator over current 2 |  | Mask: 0040h
|  |  | Generator over current 3 |  | Mask: 0020h
|  |  | Reverse / reduced power 1 |  | Mask: 0010h
|  |  | Reverse / reduced power 2 |  | Mask: 0008h
|  |  | Generator overload IOP 1 |  | Mask: 0004h
|  |  | Generator overload IOP 2 |  | Mask: 0002h
|  |  | Busbar phase rotation mismatch |  | Mask: 0001h
50128 | uint16 | 10138 | BITLIST Alarms Gen 1 latched (unacknowledged)
|  |  | 06.16 Generator unbalanced load 1 latched |  | Mask: 8000h
|  |  | 06.17 Generator unbalanced load 2 latched |  | Mask: 4000h
|  |  | 06.18 Generator voltage asymmetry latched |  | Mask: 2000h
|  |  | 06.19 Ground fault 1 latched |  | Mask: 1000h
|  |  | 06.20 Ground fault 2 latched |  | Mask: 0800h
|  |  | 06.21 Gen. Phase Rotation mismatch Latched |  | Mask: 0400h
|  |  | 06.29 Gen. active power mismatch Latched |  | Mask: 0200h
|  |  | 06.30 Generator unloading mismatch Latched |  | Mask: 0100h
|  |  | 06.22 Inverse time over current Latched |  | Mask: 0080h
|  |  | 06.31 Operating Range failed latched |  | Mask: 0040h
|  |  | 06.23 Generator overload MOP 1 latched |  | Mask: 0020h
|  |  | 06.24 Generator overload MOP 2 latched |  | Mask: 0010h
|  |  | 06.25 Gen.Power Factor lagging 1 latched |  | Mask: 0008h
|  |  | 06.26 Gen.Power Factor lagging 2 latched |  | Mask: 0004h
|  |  | 06.27 Gen.Power Factor leading 1 latched |  | Mask: 0002h
|  |  | 06.28 Gen.Power Factor leading 2 latched |  | Mask: 0001h
50129 | uint16 | 4163 | BITLIST Alarms Generator 1 active
|  |  | Generator unbalanced load 1 |  | Mask: 8000h
|  |  | Generator unbalanced load 2 |  | Mask: 4000h
|  |  | Generator voltage asymmetry |  | Mask: 2000h
|  |  | Ground fault 1 |  | Mask: 1000h
|  |  | Ground fault 2 |  | Mask: 0800h
|  |  | Gen. Phase Rotation mismatch |  | Mask: 0400h
|  |  | Gen. active power mismatch |  | Mask: 0200h
|  |  | Generator unloading mismatch |  | Mask: 0100h
|  |  | Inverse time over current |  | Mask: 0080h
|  |  | Operating Range failed |  | Mask: 0040h
|  |  | Generator overload MOP 1 |  | Mask: 0020h
|  |  | Generator overload MOP 2 |  | Mask: 0010h
|  |  | Gen.Power Factor lagging 1 |  | Mask: 0008h
|  |  | Gen.Power Factor lagging 2 |  | Mask: 0004h
|  |  | Gen.Power Factor leading 1 |  | Mask: 0002h
|  |  | Gen.Power Factor leading 2 |  | Mask: 0001h
50130 | int16 |  | Internal
50131 | int16 |  | Internal
Subtopic Mains
50132 | uint16 | 10135 | BITLIST Alarms Mains latched (unacknowledged)
|  |  | 07.06 Mains over frequency 1 latched |  | Mask: 8000h
|  |  | 07.07 Mains over frequency 2 latched |  | Mask: 4000h
|  |  | 07.08 Mains under frequency 1 latched |  | Mask: 2000h
|  |  | 07.09 Mains under frequency 2 latched |  | Mask: 1000h
|  |  | 07.10 Mains over voltage 1 latched |  | Mask: 0800h
|  |  | 07.11 Mains over voltage 2 latched |  | Mask: 0400h
|  |  | 07.12 Mains under voltage 1 latched |  | Mask: 0200h
|  |  | 07.13 Mains under voltage 2 latched |  | Mask: 0100h
|  |  | 07.14 Mains Phase shift latched |  | Mask: 0080h
|  |  | 07.25 Mains decoupling latched |  | Mask: 0040h
|  |  | 07.32 Mains AC Wiring |  | Mask: 0020h
|  |  | Internal |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | 07.05 Mains Phase rotation mismatch latched |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50133 | uint16 | 4188 | BITLIST Alarms Mains active
|  |  | Mains over frequency 1 |  | Mask: 8000h
|  |  | Mains over frequency 2 |  | Mask: 4000h
|  |  | Mains under frequency 1 |  | Mask: 2000h
|  |  | Mains under frequency 2 |  | Mask: 1000h
|  |  | Mains over voltage 1 |  | Mask: 0800h
|  |  | Mains over voltage 2 |  | Mask: 0400h
|  |  | Mains under voltage 1 |  | Mask: 0200h
|  |  | Mains under voltage 2 |  | Mask: 0100h
|  |  | Mains Phase shift |  | Mask: 0080h
|  |  | Mains decoupling |  | Mask: 0040h
|  |  | Mains AC Wiring |  | Mask: 0020h
|  |  | Internal |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | Mains Phase rotation mismatch |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50134 | uint16 | 10278 | BITLIST Alarms Mains 1 latched (unacknowledged)
|  |  | 07.21 Mains import power 1 latched |  | Mask: 8000h
|  |  | 07.22 Mains import power 2 latched |  | Mask: 4000h
|  |  | 07.23 Mains export power 1 latched |  | Mask: 2000h
|  |  | 07.24 Mains export power 2 latched |  | Mask: 1000h
|  |  | 07.17 Mains PF lagging 1 latched |  | Mask: 0800h
|  |  | 07.18 Mains PF lagging 2 latched |  | Mask: 0400h
|  |  | 07.19 Mains PF leading 1 latched |  | Mask: 0200h
|  |  | 07.20 Mains PF leading 2 latched |  | Mask: 0100h
|  |  | 07.15 Mains df/dt latched |  | Mask: 0080h
|  |  | 07.16 Mains active power mismatch latched |  | Mask: 0040h
|  |  | 07.28 Mains Time-dep. Voltage 1 (FRT) latched |  | Mask: 0020h
|  |  | 07.33 Mains Time-dep. Voltage 3 (FRT) latched |  | Mask: 0010h
|  |  | 07.27 Mains slow voltage increase (10 min) |  | Mask: 0008h
|  |  | 07.31 Mains Time-dep. Voltage 2 (FRT) latched |  | Mask: 0004h
|  |  | 07.29 Mains QV Monitoring step 1 latched |  | Mask: 0002h
|  |  | 07.30 Mains QV Monitoring step 2 latched |  | Mask: 0001h
50135 | uint16 | 4187 | BITLIST Alarms Mains 1 active
|  |  | Mains import power 1 |  | Mask: 8000h
|  |  | Mains import power 2 |  | Mask: 4000h
|  |  | Mains export power 1 |  | Mask: 2000h
|  |  | Mains export power 2 |  | Mask: 1000h
|  |  | Mains PF lagging 1 |  | Mask: 0800h
|  |  | Mains PF lagging 2 |  | Mask: 0400h
|  |  | Mains PF leading 1 |  | Mask: 0200h
|  |  | Mains PF leading 2 |  | Mask: 0100h
|  |  | Mains df/dt |  | Mask: 0080h
|  |  | Mains active power mismatch |  | Mask: 0040h
|  |  | Mains Time-dep. Voltage 1 (FRT) |  | Mask: 0020h
|  |  | Mains Time-dep. Voltage 3 (FRT) |  | Mask: 0010h
|  |  | Mains slow voltage increase (10 min) |  | Mask: 0008h
|  |  | Mains Time-dep. Voltage 2 (FRT) |  | Mask: 0004h
|  |  | QV Monitoring 1 tripped |  | Mask: 0002h
|  |  | QV Monitoring 2 tripped |  | Mask: 0001h
50136 | uint16 |  | BITLIST
|  |  | Internal |  | Mask: F000h
|  |  | Engine state 2: Off 3: Preglow 4: Crank 5: Run 6: Cool down 7: Spin down 8: Start pause 9: Idle 10: Run-up synchr. mode active 11: Run-up synchr. wait on excitation 0, 1 12, 13… : internal |  | Mask: 0F00h
|  |  | Reactive load control state 2: Static 3: Isochronous 4: Reactive load control 0, 1, 5, 6, 7, 8, 9, 11, … : internal |  | Mask: 00F0h
|  |  | Real load control state 2: Static 3: Isochronous 4: Base load control 5: Export/import control 0, 1, 6, 7, 8, 9, 10, 11, … : internal |  | Mask: 000Fh
50137 |  |  | Internal
Subtopic Digital Inputs
50138 | uint16 | 10132 | BITLIST Alarms DI 1 latched (unacknowledged)
|  |  | 09.01 Discrete input 1 latched |  | Mask: 8000h
|  |  | 09.02 Discrete input 2 latched |  | Mask: 4000h
|  |  | 09.03 Discrete input 3 latched |  | Mask: 2000h
|  |  | 09.04 Discrete input 4 latched |  | Mask: 1000h
|  |  | 09.05 Discrete input 5 latched |  | Mask: 0800h
|  |  | 09.06 Discrete input 6 latched |  | Mask: 0400h
|  |  | 09.07 Discrete input 7 latched |  | Mask: 0200h
|  |  | 09.08 Discrete input 8 latched |  | Mask: 0100h
|  |  | 09.09 Discrete input 9 latched |  | Mask: 0080h
|  |  | 09.10 Discrete input 10 latched |  | Mask: 0040h
|  |  | 09.11 Discrete input 11 latched |  | Mask: 0020h
|  |  | 09.12 Discrete input 12 latched |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50139 | uint16 | 4181 | BITLIST Alarms DI 1 active
|  |  | Discrete input 1 |  | Mask: 8000h
|  |  | Discrete input 2 |  | Mask: 4000h
|  |  | Discrete input 3 |  | Mask: 2000h
|  |  | Discrete input 4 |  | Mask: 1000h
|  |  | Discrete input 5 |  | Mask: 0800h
|  |  | Discrete input 6 |  | Mask: 0400h
|  |  | Discrete input 7 |  | Mask: 0200h
|  |  | Discrete input 8 |  | Mask: 0100h
|  |  | Discrete input 9 |  | Mask: 0080h
|  |  | Discrete input 10 |  | Mask: 0040h
|  |  | Discrete input 11 |  | Mask: 0020h
|  |  | Discrete input 12 |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50140 | uint16 | 16377 | BITLIST Alarms Ext. DI 1 latched (unacknowledged)
|  |  | 12.16 External discrete input 16 latched |  | Mask: 8000h
|  |  | 12.15 External discrete input 15 latched |  | Mask: 4000h
|  |  | 12.14 External discrete input 14 latched |  | Mask: 2000h
|  |  | 12.13 External discrete input 13 latched |  | Mask: 1000h
|  |  | 12.12 External discrete input 12 latched |  | Mask: 0800h
|  |  | 12.11 External discrete input 11 latched |  | Mask: 0400h
|  |  | 12.10 External discrete input 10 latched |  | Mask: 0200h
|  |  | 12.09 External discrete input 9 latched |  | Mask: 0100h
|  |  | 12.08 External discrete input 8 latched |  | Mask: 0080h
|  |  | 12.07 External discrete input 7 latched |  | Mask: 0040h
|  |  | 12.06 External discrete input 6 latched |  | Mask: 0020h
|  |  | 12.05 External discrete input 5 latched |  | Mask: 0010h
|  |  | 12.04 External discrete input 4 latched |  | Mask: 0008h
|  |  | 12.03 External discrete input 3 latched |  | Mask: 0004h
|  |  | 12.02 External discrete input 2 latched |  | Mask: 0002h
|  |  | 12.01 External discrete input 1 latched |  | Mask: 0001h
50141 | uint16 | 4185 | BITLIST Alarms Ext. DI 1 active
|  |  | External discrete input 16 |  | Mask: 8000h
|  |  | External discrete input 15 |  | Mask: 4000h
|  |  | External discrete input 14 |  | Mask: 2000h
|  |  | External discrete input 13 |  | Mask: 1000h
|  |  | External discrete input 12 |  | Mask: 0800h
|  |  | External discrete input 11 |  | Mask: 0400h
|  |  | External discrete input 10 |  | Mask: 0200h
|  |  | External discrete input 9 |  | Mask: 0100h
|  |  | External discrete input 8 |  | Mask: 0080h
|  |  | External discrete input 7 |  | Mask: 0040h
|  |  | External discrete input 6 |  | Mask: 0020h
|  |  | External discrete input 5 |  | Mask: 0010h
|  |  | External discrete input 4 |  | Mask: 0008h
|  |  | External discrete input 3 |  | Mask: 0004h
|  |  | External discrete input 2 |  | Mask: 0002h
|  |  | External discrete input 1 |  | Mask: 0001h
50142 | uint16 | 10284 | BITLIST Alarm Ext. DI 2 latched (unacknowledged)
|  |  | 12.32 External discrete input 32 latched |  | Mask: 8000h
|  |  | 12.31 External discrete input 31 latched |  | Mask: 4000h
|  |  | 12.30 External discrete input 30 latched |  | Mask: 2000h
|  |  | 12.29 External discrete input 29 latched |  | Mask: 1000h
|  |  | 12.28 External discrete input 28 latched |  | Mask: 0800h
|  |  | 12.27 External discrete input 27 latched |  | Mask: 0400h
|  |  | 12.26 External discrete input 26 latched |  | Mask: 0200h
|  |  | 12.25 External discrete input 25 latched |  | Mask: 0100h
|  |  | 12.24 External discrete input 24 latched |  | Mask: 0080h
|  |  | 12.23 External discrete input 23 latched |  | Mask: 0040h
|  |  | 12.22 External discrete input 22 latched |  | Mask: 0020h
|  |  | 12.21 External discrete input 21 latched |  | Mask: 0010h
|  |  | 12.20 External discrete input 20 latched |  | Mask: 0008h
|  |  | 12.19 External discrete input 19 latched |  | Mask: 0004h
|  |  | 12.18 External discrete input 18 latched |  | Mask: 0002h
|  |  | 12.17 External discrete input 17 latched |  | Mask: 0001h
50143 | uint16 | 4195 | BITLIST Alarm Ext. DI 2 active
|  |  | External discrete input 32 |  | Mask: 8000h
|  |  | External discrete input 31 |  | Mask: 4000h
|  |  | External discrete input 30 |  | Mask: 2000h
|  |  | External discrete input 29 |  | Mask: 1000h
|  |  | External discrete input 28 |  | Mask: 0800h
|  |  | External discrete input 27 |  | Mask: 0400h
|  |  | External discrete input 26 |  | Mask: 0200h
|  |  | External discrete input 25 |  | Mask: 0100h
|  |  | External discrete input 24 |  | Mask: 0080h
|  |  | External discrete input 23 |  | Mask: 0040h
|  |  | External discrete input 22 |  | Mask: 0020h
|  |  | External discrete input 21 |  | Mask: 0010h
|  |  | External discrete input 20 |  | Mask: 0008h
|  |  | External discrete input 19 |  | Mask: 0004h
|  |  | External discrete input 18 |  | Mask: 0002h
|  |  | External discrete input 17 |  | Mask: 0001h
50144 | uint16 | 10283 | BITLIST Alarms DI 2 latched (unacknowledged)
|  |  | 09.13 Discrete input 13 latched |  | Mask: 8000h
|  |  | 09.14 Discrete input 14 latched |  | Mask: 4000h
|  |  | 09.15 Discrete input 15 latched |  | Mask: 2000h
|  |  | 09.16 Discrete input 16 latched |  | Mask: 1000h
|  |  | 09.17 Discrete input 17 latched |  | Mask: 0800h
|  |  | 09.18 Discrete input 18 latched |  | Mask: 0400h
|  |  | 09.19 Discrete input 19 latched |  | Mask: 0200h
|  |  | 09.20 Discrete input 20 latched |  | Mask: 0100h
|  |  | 09.21 Discrete input 21 latched |  | Mask: 0080h
|  |  | 09.22 Discrete input 22 latched |  | Mask: 0040h
|  |  | 09.23 Discrete input 23 latched |  | Mask: 0020h
|  |  | Internal |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50145 | uint16 | 4183 | BITLIST Alarms DI 2 active
|  |  | Discrete input 13 |  | Mask: 8000h
|  |  | Discrete input 14 |  | Mask: 4000h
|  |  | Discrete input 15 |  | Mask: 2000h
|  |  | Discrete input 16 |  | Mask: 1000h
|  |  | Discrete input 17 |  | Mask: 0800h
|  |  | Discrete input 18 |  | Mask: 0400h
|  |  | Discrete input 19 |  | Mask: 0200h
|  |  | Discrete input 20 |  | Mask: 0100h
|  |  | Discrete input 21 |  | Mask: 0080h
|  |  | Discrete input 22 |  | Mask: 0040h
|  |  | Discrete input 23 |  | Mask: 0020h
|  |  | Internal |  | Mask: 0010h
|  |  | Internal |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Internal |  | Mask: 0002h
|  |  | Internal |  | Mask: 0001h
50146 | int16 |  | Internal
50147 | int16 |  | Internal
50148 | int16 |  | Internal
50149 | int16 |  | Internal
Subtopic Flexible Thresholds
50150 | uint16 | 10279 | BITLIST Alarms Flex.Thresholds 1-16 latched
|  |  | 15.16 Flexible limit 16 latched |  | Mask: 8000h
|  |  | 15.15 Flexible limit 15 latched |  | Mask: 4000h
|  |  | 15.14 Flexible limit 14 latched |  | Mask: 2000h
|  |  | 15.13 Flexible limit 13 latched |  | Mask: 1000h
|  |  | 15.12 Flexible limit 12 latched |  | Mask: 0800h
|  |  | 15.11 Flexible limit 11 latched |  | Mask: 0400h
|  |  | 15.10 Flexible limit 10 latched |  | Mask: 0200h
|  |  | 15.09 Flexible limit 9 latched |  | Mask: 0100h
|  |  | 15.08 Flexible limit 8 latched |  | Mask: 0080h
|  |  | 15.07 Flexible limit 7 latched |  | Mask: 0040h
|  |  | 15.06 Flexible limit 6 latched |  | Mask: 0020h
|  |  | 15.05 Flexible limit 5 latched |  | Mask: 0010h
|  |  | 15.04 Flexible limit 4 latched |  | Mask: 0008h
|  |  | 15.03 Flexible limit 3 latched |  | Mask: 0004h
|  |  | 15.02 Flexible limit 2 latched |  | Mask: 0002h
|  |  | 15.01 Flexible limit 1 latched |  | Mask: 0001h
50151 | uint16 | 4175 | BITLIST Alarms Flex.Thresholds 1-16 active
|  |  | Flexible limit 16 |  | Mask: 8000h
|  |  | Flexible limit 15 |  | Mask: 4000h
|  |  | Flexible limit 14 |  | Mask: 2000h
|  |  | Flexible limit 13 |  | Mask: 1000h
|  |  | Flexible limit 12 |  | Mask: 0800h
|  |  | Flexible limit 11 |  | Mask: 0400h
|  |  | Flexible limit 10 |  | Mask: 0200h
|  |  | Flexible limit 9 |  | Mask: 0100h
|  |  | Flexible limit 8 |  | Mask: 0080h
|  |  | Flexible limit 7 |  | Mask: 0040h
|  |  | Flexible limit 6 |  | Mask: 0020h
|  |  | Flexible limit 5 |  | Mask: 0010h
|  |  | Flexible limit 4 |  | Mask: 0008h
|  |  | Flexible limit 3 |  | Mask: 0004h
|  |  | Flexible limit 2 |  | Mask: 0002h
|  |  | Flexible limit 1 |  | Mask: 0001h
50152 | uint16 | 10280 | BITLIST Alarms Flex.Thresholds 17-32 latched
|  |  | 15.32 Flexible limit 32 latched |  | Mask: 8000h
|  |  | 15.31 Flexible limit 31 latched |  | Mask: 4000h
|  |  | 15.30 Flexible limit 30 latched |  | Mask: 2000h
|  |  | 15.29 Flexible limit 29 latched |  | Mask: 1000h
|  |  | 15.28 Flexible limit 28 latched |  | Mask: 0800h
|  |  | 15.27 Flexible limit 27 latched |  | Mask: 0400h
|  |  | 15.26 Flexible limit 26 latched |  | Mask: 0200h
|  |  | 15.25 Flexible limit 25 latched |  | Mask: 0100h
|  |  | 15.24 Flexible limit 24 latched |  | Mask: 0080h
|  |  | 15.23 Flexible limit 23 latched |  | Mask: 0040h
|  |  | 15.22 Flexible limit 22 latched |  | Mask: 0020h
|  |  | 15.21 Flexible limit 21 latched |  | Mask: 0010h
|  |  | 15.20 Flexible limit 20 latched |  | Mask: 0008h
|  |  | 15.19 Flexible limit 19 latched |  | Mask: 0004h
|  |  | 15.18 Flexible limit 18 latched |  | Mask: 0002h
|  |  | 15.17 Flexible limit 17 latched |  | Mask: 0001h
50153 | uint16 | 4177 | BITLIST Alarms Flex.Thresholds 17-32 active
|  |  | Flexible limit 32 |  | Mask: 8000h
|  |  | Flexible limit 31 |  | Mask: 4000h
|  |  | Flexible limit 30 |  | Mask: 2000h
|  |  | Flexible limit 29 |  | Mask: 1000h
|  |  | Flexible limit 28 |  | Mask: 0800h
|  |  | Flexible limit 27 |  | Mask: 0400h
|  |  | Flexible limit 26 |  | Mask: 0200h
|  |  | Flexible limit 25 |  | Mask: 0100h
|  |  | Flexible limit 24 |  | Mask: 0080h
|  |  | Flexible limit 23 |  | Mask: 0040h
|  |  | Flexible limit 22 |  | Mask: 0020h
|  |  | Flexible limit 21 |  | Mask: 0010h
|  |  | Flexible limit 20 |  | Mask: 0008h
|  |  | Flexible limit 19 |  | Mask: 0004h
|  |  | Flexible limit 18 |  | Mask: 0002h
|  |  | Flexible limit 17 |  | Mask: 0001h
50154 | uint16 | 10281 | BITLIST Alarms Flex.Thresholds 33-40 latched
|  |  | Internal |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Internal |  | Mask: 0100h
|  |  | 15.40 Flexible limit 40 latched |  | Mask: 0080h
|  |  | 15.39 Flexible limit 39 latched |  | Mask: 0040h
|  |  | 15.38 Flexible limit 38 latched |  | Mask: 0020h
|  |  | 15.37 Flexible limit 37 latched |  | Mask: 0010h
|  |  | 15.36 Flexible limit 36 latched |  | Mask: 0008h
|  |  | 15.35 Flexible limit 35 latched |  | Mask: 0004h
|  |  | 15.34 Flexible limit 34 latched |  | Mask: 0002h
|  |  | 15.33 Flexible limit 33 latched |  | Mask: 0001h
50155 | uint16 | 4179 | BITLIST Alarms Flex.Thresholds 33-40 active
|  |  | Internal |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Internal |  | Mask: 0100h
|  |  | Flexible limit 40 |  | Mask: 0080h
|  |  | Flexible limit 39 |  | Mask: 0040h
|  |  | Flexible limit 38 |  | Mask: 0020h
|  |  | Flexible limit 37 |  | Mask: 0010h
|  |  | Flexible limit 36 |  | Mask: 0008h
|  |  | Flexible limit 35 |  | Mask: 0004h
|  |  | Flexible limit 34 |  | Mask: 0002h
|  |  | Flexible limit 33 |  | Mask: 0001h
50156 |  |  | Internal
50157 |  |  | Internal
50158 |  |  | Internal
Subtopic DC Analogue Values Wirebreak
50159 | uint16 | 10137 | BITLIST Alarms AI Wire Break latched
|  |  | Internal |  | Mask: 0001h
|  |  | 10.01 Analog input 1 wire break |  | Mask: 0002h
|  |  | 10.02 Analog input 2 wire break |  | Mask: 0004h
|  |  | 10.03 Analog input 3 wire break |  | Mask: 0008h
|  |  | 10.04 Analog input 4 wire break |  | Mask: 0010h
|  |  | 10.05 Analog input 5 wire break |  | Mask: 0020h
|  |  | 10.06 Analog input 6 wire break |  | Mask: 0040h
|  |  | 10.07 Analog input 7 wire break |  | Mask: 0080h
|  |  | 10.08 Analog input 8 wire break |  | Mask: 0100h
|  |  | 10.09 Analog input 9 wire break |  | Mask: 0200h
|  |  | 10.10 Analog input 10 wire break |  | Mask: 0400h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 8000h
50160 | uint16 | 4173 | BITLIST Alarms AI Wire Break active
|  |  | Internal |  | Mask: 0001h
|  |  | Analog input 1 wire break |  | Mask: 0002h
|  |  | Analog input 2 wire break |  | Mask: 0004h
|  |  | Analog input 3 wire break |  | Mask: 0008h
|  |  | Analog input 4 wire break |  | Mask: 0010h
|  |  | Analog input 5 wire break |  | Mask: 0020h
|  |  | Analog input 6 wire break |  | Mask: 0040h
|  |  | Analog input 7 wire break |  | Mask: 0080h
|  |  | Analog input 8 wire break |  | Mask: 0100h
|  |  | Analog input 9 wire break |  | Mask: 0200h
|  |  | Analog input 10 wire break |  | Mask: 0400h
|  |  | Internal |  | Mask: 0800h
|  |  | Internal |  | Mask: 1000h
|  |  | Internal |  | Mask: 2000h
|  |  | Internal |  | Mask: 4000h
|  |  | Internal |  | Mask: 8000h
50161 | uint16 | 10285 | BITLIST Alarms Ext.AI Wire Break latched
|  |  | 25.01 Ext. analog input 1 wire break |  | Mask: 0001h
|  |  | 25.02 Ext. analog input 2 wire break |  | Mask: 0002h
|  |  | 25.03 Ext. analog input 3 wire break |  | Mask: 0004h
|  |  | 25.04 Ext. analog input 4 wire break |  | Mask: 0008h
|  |  | 25.05 Ext. analog input 5 wire break |  | Mask: 0010h
|  |  | 25.06 Ext. analog input 6 wire break |  | Mask: 0020h
|  |  | 25.07 Ext. analog input 7 wire break |  | Mask: 0040h
|  |  | 25.08 Ext. analog input 8 wire break |  | Mask: 0080h
|  |  | 25.09 Ext. analog input 9 wire break |  | Mask: 0100h
|  |  | 25.10 Ext. analog input 10 wire break |  | Mask: 0200h
|  |  | 25.11 Ext. analog input 11 wire break |  | Mask: 0400h
|  |  | 25.12 Ext. analog input 12 wire break |  | Mask: 0800h
|  |  | 25.13 Ext. analog input 13 wire break |  | Mask: 1000h
|  |  | 25.14 Ext. analog input 14 wire break |  | Mask: 2000h
|  |  | 25.15 Ext. analog input 15 wire break |  | Mask: 4000h
|  |  | 25.16 Ext. analog input 16 wire break |  | Mask: 8000h
50162 | uint16 | 4196 | BITLIST Alarms Ext.AI Wire Break active
|  |  | Ext. analog input 1 wire break |  | Mask: 0001h
|  |  | Ext. analog input 2 wire break |  | Mask: 0002h
|  |  | Ext. analog input 3 wire break |  | Mask: 0004h
|  |  | Ext. analog input 4 wire break |  | Mask: 0008h
|  |  | Ext. analog input 5 wire break |  | Mask: 0010h
|  |  | Ext. analog input 6 wire break |  | Mask: 0020h
|  |  | Ext. analog input 7 wire break |  | Mask: 0040h
|  |  | Ext. analog input 8 wire break |  | Mask: 0080h
|  |  | Ext. analog input 9 wire break |  | Mask: 0100h
|  |  | Ext. analog input 10 wire break |  | Mask: 0200h
|  |  | Ext. analog input 11 wire break |  | Mask: 0400h
|  |  | Ext. analog input 12 wire break |  | Mask: 0800h
|  |  | Ext. analog input 13 wire break |  | Mask: 1000h
|  |  | Ext. analog input 14 wire break |  | Mask: 2000h
|  |  | Ext. analog input 15 wire break |  | Mask: 4000h
|  |  | Ext. analog input 16 wire break |  | Mask: 8000h
50163 |  |  | Internal
50164 |  |  | Internal
Subtopic Other Alarms
50165 | uint16 | 10286 | BITLIST Other Alarms 1 latched (unacknowledged)
|  |  | 08.53 LS interface redundancy latched |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Free alarm 4 |  | Mask: 2000h
|  |  | Free alarm 3 |  | Mask: 1000h
|  |  | Free alarm 2 |  | Mask: 0800h
|  |  | Free alarm 1 |  | Mask: 0400h
|  |  | 05.21 Max. starts per time |  | Mask: 0200h
|  |  | 17.09 Neutral interl. reply mismatch latched |  | Mask: 0100h
|  |  | 17.08 Decoupling GCB-MCB latched |  | Mask: 0080h
|  |  | 17.07 Measurement difference 4105 latched |  | Mask: 0040h
|  |  | 17.06 Parameter alignment 4105 latched |  | Mask: 0020h
|  |  | 17.05 Missing member 4105 latched |  | Mask: 0010h
|  |  | 08.22 Busbar v/f not ok latched |  | Mask: 0008h
|  |  | 08.21 Feedback GCB mismatch latched |  | Mask: 0004h
|  |  | 17.02 Reactive load share mismatch latched |  | Mask: 0002h
|  |  | 17.01 Active load share mismatch latched |  | Mask: 0001h
50166 | uint16 | 5197 | BITLIST Other Alarms 1 active
|  |  | LS interface redundancy active |  | Mask: 8000h
|  |  | Internal |  | Mask: 4000h
|  |  | Free alarm 4 active |  | Mask: 2000h
|  |  | Free alarm 3 active |  | Mask: 1000h
|  |  | Free alarm 2 active |  | Mask: 0800h
|  |  | Free alarm 1 active |  | Mask: 0400h
|  |  | Internal |  | Mask: 0200h
|  |  | Neutral contactor failure active |  | Mask: 0100h
|  |  | Decoupling GCB-MCB active |  | Mask: 0080h
|  |  | Meas.difference 4105 VDE-AR-N 4105 active |  | Mask: 0040h
|  |  | Parameter alignment VDE-AR-N 4105 active |  | Mask: 0020h
|  |  | Missing member VDE-AR-N 4105 active |  | Mask: 0010h
|  |  | Busbar monitoring latched active |  | Mask: 0008h
|  |  | Internal |  | Mask: 0004h
|  |  | Reactive load sharing mismatch latched |  | Mask: 0002h
|  |  | Active load sharing mismatch latched |  | Mask: 0001h
50167 | uint16 | 4085 | BITLIST Internal Flags 1-16
|  |  | 96.16 LM Internal Flag 16 |  | Mask: 8000h
|  |  | 96.15 LM Internal Flag 15 |  | Mask: 4000h
|  |  | 96.14 LM Internal Flag 14 |  | Mask: 2000h
|  |  | 96.13 LM Internal Flag 13 |  | Mask: 1000h
|  |  | 96.12 LM Internal Flag 12 |  | Mask: 0800h
|  |  | 96.11 LM Internal Flag 11 |  | Mask: 0400h
|  |  | 96.10 LM Internal Flag 10 |  | Mask: 0200h
|  |  | 96.09 LM Internal Flag 9 |  | Mask: 0100h
|  |  | 96.08 LM Internal Flag 8 |  | Mask: 0080h
|  |  | 96.07 LM Internal Flag 7 |  | Mask: 0040h
|  |  | 96.06 LM Internal Flag 6 |  | Mask: 0020h
|  |  | 96.05 LM Internal Flag 5 |  | Mask: 0010h
|  |  | 96.04 LM Internal Flag 4 |  | Mask: 0008h
|  |  | 96.03 LM Internal Flag 3 |  | Mask: 0004h
|  |  | 96.02 LM Internal Flag 2 |  | Mask: 0002h
|  |  | 96.01 LM Internal Flag 1 |  | Mask: 0001h
50168 | uint16 | 4095 | BITLIST Internal Flags 17-32
|  |  | 96.32 LM Internal Flag 32 |  | Mask: 8000h
|  |  | 96.31 LM Internal Flag 31 |  | Mask: 4000h
|  |  | 96.30 LM Internal Flag 30 |  | Mask: 2000h
|  |  | 96.29 LM Internal Flag 29 |  | Mask: 1000h
|  |  | 96.28 LM Internal Flag 28 |  | Mask: 0800h
|  |  | 96.27 LM Internal Flag 27 |  | Mask: 0400h
|  |  | 96.26 LM Internal Flag 26 |  | Mask: 0200h
|  |  | 96.25 LM Internal Flag 25 |  | Mask: 0100h
|  |  | 96.24 LM Internal Flag 24 |  | Mask: 0080h
|  |  | 96.23 LM Internal Flag 23 |  | Mask: 0040h
|  |  | 96.22 LM Internal Flag 22 |  | Mask: 0020h
|  |  | 96.21 LM Internal Flag 21 |  | Mask: 0010h
|  |  | 96.20 LM Internal Flag 20 |  | Mask: 0008h
|  |  | 96.19 LM Internal Flag 19 |  | Mask: 0004h
|  |  | 96.18 LM Internal Flag 18 |  | Mask: 0002h
|  |  | 96.17 LM Internal Flag 17 |  | Mask: 0001h
50169 | uint16 | 10282 | BITLIST Free Alarms 1 latched (unacknowledged)
|  |  | 16.16 Free alarm 16 latched |  | Mask: 8000h
|  |  | 16.15 Free alarm 15 latched |  | Mask: 4000h
|  |  | 16.14 Free alarm 14 latched |  | Mask: 2000h
|  |  | 16.13 Free alarm 13 latched |  | Mask: 1000h
|  |  | 16.12 Free alarm 12 latched |  | Mask: 0800h
|  |  | 16.11 Free alarm 11 latched |  | Mask: 0400h
|  |  | 16.10 Free alarm 10 latched |  | Mask: 0200h
|  |  | 16.09 Free alarm 9 latched |  | Mask: 0100h
|  |  | 16.08 Free alarm 8 latched |  | Mask: 0080h
|  |  | 16.07 Free alarm 7 latched |  | Mask: 0040h
|  |  | 16.06 Free alarm 6 latched |  | Mask: 0020h
|  |  | 16.05 Free alarm 5 latched |  | Mask: 0010h
|  |  | 16.04 Free alarm 4 latched |  | Mask: 0008h
|  |  | 16.03 Free alarm 3 latched |  | Mask: 0004h
|  |  | 16.02 Free alarm 2 latched |  | Mask: 0002h
|  |  | 16.01 Free alarm 1 latched |  | Mask: 0001h
50170 | uint16 | 4194 | BITLIST Free Alarms 1 active
|  |  | Free alarm 16 active |  | Mask: 8000h
|  |  | Free alarm 15 active |  | Mask: 4000h
|  |  | Free alarm 14 active |  | Mask: 2000h
|  |  | Free alarm 13 active |  | Mask: 1000h
|  |  | Free alarm 12 active |  | Mask: 0800h
|  |  | Free alarm 11 active |  | Mask: 0400h
|  |  | Free alarm 10 active |  | Mask: 0200h
|  |  | Free alarm 9 active |  | Mask: 0100h
|  |  | Free alarm 8 active |  | Mask: 0080h
|  |  | Free alarm 7 active |  | Mask: 0040h
|  |  | Free alarm 6 active |  | Mask: 0020h
|  |  | Free alarm 5 active |  | Mask: 0010h
|  |  | Free alarm 4 active |  | Mask: 0008h
|  |  | Free alarm 3 active |  | Mask: 0004h
|  |  | Free alarm 2 active |  | Mask: 0002h
|  |  | Free alarm 1 active |  | Mask: 0001h